## Slide 1: Hidden Energy. Real Returns.
Staged Waste Heat Recovery and Heat Pump, as a System
Case study Gundagai Meat Processors

## Slide 2: Gundagai Meat Processors
One of Australia’s leading lamb processors
Established in 1974 By the Barton family. A family-owned lamb processor based in Gundagai, NSW
~1M sheep & lambs 25,000 t/HSCW processed annually
350 (FTE) employees
~20 active exporting countries
Trusted partnerships Built on innovation, quality and long-term partnerships with producers and customers.
Energy & refrigeration systems Operates a medium-sized ammonia refrigeration system alongside gas-fired hot water generation for sterilisation, sanitation and cleaning.

## Slide 3: Gundagai Meat Processors
One of Australia’s leading lamb processors
Trusted partnerships Built on innovation, quality and long-term partnerships with producers and customers.
Energy & refrigeration systems Operates a medium-sized ammonia refrigeration system alongside gas-fired hot water generation for sterilisation, sanitation and cleaning.
Established in 1974 By the Barton family. A family-owned lamb processor based in Gundagai, NSW
~1M sheep & lambs 25,000 t/HSCW processed annually
350 (FTE) employees
~20 active exporting countries

## Slide 4: GMP Challenges
Capacity Under Pressure
Looming Capital Cost
Rising Gas Prices
Rising costs and ageing infrastructure could no longer be solved by adding boiler capacity alone

## Slide 5: GMP Challenges
Capacity Under Pressure
Looming Capital Cost
Rising Gas Prices
Rising costs and ageing infrastructure could no longer be solved by adding boiler capacity alone
2 MW boiler Regularly operating at or above capacity
15°C winter water Increased heating demand
82°C sterilisation temperature Difficult to maintain occasionally interrupting production
$400,000 capital cost To upgrade the existing boiler
2.5 MW boiler Required to keep pace with production growth, with no improvement to energy efficiency
+50% Increase in GMP’s gas price at contract renewal
$18/GJ Representative delivered gas price with little near-term relief

## Slide 6
THE PROBLEM
This combination of rising fuel costs and looming capital expenditure prompted GMP to look for an alternative to simply increasing boiler capacity.
THE SOLUTION
A Staged Heat Recovery and Heat Pump

## Slide 7: A Staged Heat Recovery Philosophy
15°C
Every degree gained passively reduces the energy needed at the next stage
Stage 1A Condenser & Oil Cooling
IN OPERATION
50°C
Closed-loop, isolated water circuit — plate heat exchangers, continuous pH monitoring, automated alarms and independent isolation valves keep process water fully protected from refrigeration fluids.
15°C
50°C
CONDENSER
OIL COOLING

## Slide 8
52.5°C
Stage 1B Compressed Air Recovery
FUTURE
A Staged Heat Recovery Philosophy
Every degree gained passively reduces the energy needed at the next stage
50°C
Closed-loop, isolated water circuit — plate heat exchangers, continuous pH monitoring, automated alarms and independent isolation valves keep process water fully protected from refrigeration fluids.
15°C
50°C
52.5°C
COMPRESSED AIR RECOVERY
CONDENSER
OIL COOLING

## Slide 9
52.5°C
Stage 2 Industrial Heat Pump
FUTURE
A Staged Heat Recovery Philosophy
Every degree gained passively reduces the energy needed at the next stage
Closed-loop, isolated water circuit — plate heat exchangers, continuous pH monitoring, automated alarms and independent isolation valves keep process water fully protected from refrigeration fluids.
88°C
50°C
88°C
INDUSTRIAL HEAT PUMP
COMPRESSED AIR RECOVERY
CONDENSER
OIL COOLING
15°C
52.5°C

## Slide 10: Stage 1A Condenser & Oil Cooling Recovery
The system operating today

## Slide 11: Performance
Combined
IN OPERATION
STAGE 1A
Condenser + Oil Cooler
CONDENSER
OIL COOLING
STAGE 2
Heat Pump
INDUSTRIAL HEAT PUMP
FUTURE
STAGE 1B
Compressed Air
COMPRESSED AIR RECOVERY
Avg heating load | 671.3 kW | 68.0 kW | 721.4 kW | 1460.6 kW
Cooling load |  |  | 478.0 kW | 478.0 kW
Power | 3.0 kW | 0.5 kW | 113.0 kW | 116.5 kW
Heating | 223.75 | 135.92 | 6.38 | 12.54
Cooling |  |  | 4.23 | 4.10
Combined | 223.75 | 135.92 | 10.61 | 16.64
Gas offset | ~ 30 % | ~ 4 % | ~ 66 % | 100 %
Coefficient of performance

## Slide 12: Forecast Financial Performance
Cost-Avoidance Basis
Cash-positive
From day one
~$400,000
Avoided boiler upgrade
~$96,000
Unrealised condenser capacity avoidance
$118,000
TOTAL
Future stages
SAVINGS PER YEAR
$10,000 Stage 1B
$108,000 Stage 2
Additional savings expected as future stages further increase gas displacement and system efficiency.
$496,000
TOTAL
Capital costs
AVOIDED
$400,000 Boiler
$96,000 Condenser capacity
$150,800
TOTAL
Operational savings
PER YEAR
$135,500 Gas
$7,100 Condenser power
$6,900 Condenser water use
$1,300 Wastewater discharge
Stage 1A measured and estimated benefits
All values are approximate

## Slide 13: Return on Investment
Cost-Avoidance Basis
Cash-positive
From day one
~$400,000
Avoided boiler upgrade
~$96,000
Condenser capacity avoidance
Project Cost $450,000
Utility Savings Only
3 years
~$150,800
$540/day 30 GJ/day
Approximate payback
Combined utility savings
Gas savings

## Slide 14: Return on Investment
Cost-Avoidance Basis
Cash-positive
From day one
~$400,000
Avoided boiler upgrade
~$96,000
Condenser capacity avoidance
Utility Savings + Incentives
2 years
~$150,000
Approximate payback
Benefit from energy efficiency certificates (ESCs)
Project Cost $450,000
Utility Savings Only
3 years
~$150,800
$540/day 30 GJ/day
Approximate payback
Combined utility savings
Gas savings

## Slide 15: Return on Investment
Utility Savings Only
3 years
~$150,800
$540/day 30 GJ/day
Approximate payback
Combined utility savings
Gas savings
Stage 1 Non Render
STAGE 1A
STAGE 1B
COMPRESSED AIR RECOVERY
OIL COOLING
CONDENSER
ESCs NSW Energy Savings Certificates VEECs Victorian Energy Efficiency Certificates ACCUs Australian Carbon Credit Units
Utility Savings + Incentives
2 years
~$150,000
Approximate payback
Benefit from energy efficiency certificates (ESCs)
Eligible incentive mechanisms
Subject to jurisdictional requirements
Project Cost $450,000

## Slide 16: Industry Learning
Stage 1 Non Render
Condensers
Oil coolers
Compressed air
STAGE 1A
STAGE 1B
Doing Stage 1 first lowers the equipment size and running cost of Stage 2
NO ACTIVE HEAT PUMP REQUIRED
Passive recovery from
Less capacity
Lower capital cost
Lower running cost
Higher baseline temperature requires
COMPRESSED AIR RECOVERY
OIL COOLING
CONDENSER

## Slide 17: Industry Learning
Stage 2
Doing Stage 1 first lowers the equipment size and running cost of Stage 2
Less capacity
Lower capital cost
Lower running cost
Higher baseline temperature requires
Every gigajoule of waste heat recovered is a gigajoule of natural gas that no longer needs to be purchased or combusted.
INDUSTRIAL HEAT PUMP
COMPRESSED AIR RECOVERY
OIL COOLING
CONDENSER

## Slide 18: Site Summary
Less capacity
Lower capital cost
Lower running cost
Higher baseline temperature requires
Doing Stage 1 first lowers the equipment size and running cost of Stage 2
Every gigajoule of waste heat recovered is a gigajoule of natural gas that no longer needs to be purchased or combusted.
RESULTS

## Slide 19: Natural Gas Reduction
Chart: Boiler Gas Use — Heat Recovery ON vs OFF
| Tue (OFF) | Wed (ON) | Thu (OFF) | Fri (ON)
Gas Use (GJ/day, indicative) | 94 | 64 | 94 | 64
Monthly SCADA trends confirm average gas consumption has fallen consistently since heat recovery began operating.
Controlled ON/OFF testing confirmed sustained savings
30 GJ/day
Average gas reduction
32% overall
7,530 GJ/annum
Estimated gas savings
$135,500/annum
$540/day
Estimated cost saving

## Slide 20: Plant Monthly Gas Usage Gigajoule
System ON Gas Usage GJ per operating day
Note
Reading Variance is due to the read date of the month
GJ Per Operating Day
Clearly see the average usage is coming down since starting the heat recovery in October
Average operating day usage since heat recovery turn on
Average operating day usage before heat recovery turn on

## Slide 21
Onsite Improvements & Performance
What GMP has seen on the ground since Stage 1A went live
Free heat
Heat recovered from refrigeration condensers and compressor oil coolers that was previously rejected to atmosphere.
Minimal maintenance or management
Fully automatic control via SCADA/PLC. “I have been impressed with how little attention the system requires, it just works.”
Extra condenser capacity
The system acts like an additional condenser, removing heat from hot ammonia gas, equivalent to roughly 400 kW of extra capacity.
Improved boiler performance
Boiler cycles steadily between high and low fire instead of running continuously at high fire.

## Slide 22: Thank You
Questions & Discussion
Project support and industry funding
Design, delivery and commissioning
Engineering and equipment